# Tender text for presence detectors

# Presence detector theRonda S360 KNX FLAT DE WH / GR

Passive-infrared presence detector for ceiling installation; flat design; automatic presence and brightness-dependent control for lighting and HVAC; round 360° detection area, walking up to 64 m2 (Ø 9 m), installation height up to 4 m;

Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs;

Energy consumption approx. 8 mA/9 mA with LED on; protection rating IP 54 (when installed); operating temperature -15° C to +50° C;

2 channels for light C1, C2; switched mode or constant light control with standby functionality (orientation light); switched mode with dimmable lighting; can be switched as operation as fully or semi-automatic; brightness switching value or setpoint adjustable in lux via parameter, object or remote control; teach-in of brightness switching value or setpoint; self-learning time delay adjustable via parameter; reduction of time delay during brief presence (brief presence); manual override by means of telegram or remote control;

2 channels for presence C4, C5, individually programmable; switch-on delay and time delay adjustable;

Separate disable object for light and presence channel; recording and transmitting of the current brightness; simple comparison of the brightness measurement by entering the measured lux value; configurable sensitivity in 5 stages; test mode to check function and detection area; scenes; extension of detection area by parallel switching of several motion detectors (master/slave or master/master); can be configured remotely with remote control;

Installation in hollow ceilings with springs, ceiling cut-out Ø 62 – 70 mm, installation depth approx. 52 mm.

Manufacturer: 	thebenHTS

Type: 		theRonda S360 KNX FLAT DE

Order no.: 	2089560 (theRonda S360 KNX FLAT DE WH, white)

2089561 (theRonda S360 KNX FLAT DE GR, grey)

Unit: ST

### Accessories

### Management remote control "SendoPro 868-A"

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote-controlled thebenHTS presence detectors.

Order no.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911