# Tender text

# Optical presence detector thePixa P360 KNX UP WH

Order No. white: 		2269200

Features:

- General information:

- Optical presence detector for ceiling installation

- KNX Data Secure

- Rectangular detection area with up to 6 flexible detection zones 
(Total area 11.0 x 15.5 m │171 m2; at 4.5 m installation height)

- Restriction of the detection area via app (thePixa Plug)

- Automatic presence and brightness-dependent control for lighting and HVAC

- Each detection zone has its own light measurement

- Adjustment of brightness measurements via thePixa Plug app

- Configurable sensitivity of sensor

- Distinction between motion and presence

- Parallel switching of multiple presence detectors (Master/Slave or Master/Master)

- Test mode for checking function and detection area via app (thePixa Plug)

- Output of occupancy rate and occupancy density via telegram

- Integrated temperature sensor

- Ceiling installation in flush-mounting box (2-point fixing)

- Surface mounting on ceilings possible with surface frame (option)

- thePixa Plug app for settings and evaluations (iOS/Android)

- KNX firmware update possible (ETS app)

- Sensor firmware update possible (thePixa Plug app)

- 6 channels light, Z1 light – Z6 light:

- Switching or constant lighting control with 6 independent control systems and standby function (orientation light)

- Switching mode with dimmable lighting

- Free switch object with configuration type switching

- Fully or semi-automatic device

- Brightness switching value configurable in lux by using parameters

- Brightness switching value configurable in lux by using parameters and telegram

- Light time delay configurable by using parameters

- Aura effect for better orientation and greater safety

- Manual override by telegram

- 6 channels HKL, Z1 HKL – Z6 HKL:

- Configurable switch-on delay and time delay

- Sending of operating mode

- Separate block telegram

- 6 channels room occupancy, Z1 room occupancy – Z6 room occupancy:

- Output of number of persons

- Control of a fan with up to 3 stages

- 3 configurable thresholds (threshold switch)

Technical data:

Operating voltage: 		230 – 240 V AC, 50 Hz

Input power (230 V):		Day mode: typ. 0.9 W

Night mode: typ. 1.6 W

Bus voltage KNX:		30 V DC

KNX bus power input: 		< 10 mA

Stationary detection area:	5.0 x 7.0 m (IH 3.0 m)

Moving detection area: 	7.5 m x 10.5 m tangential / radial (IH 3.0 m)

Installation height Mh: 		2.5 – 4.5 m

Brightness switching value:	5 – 3000 lux / measurement off

Brightness set point value: 	5 – 3000 lux / light off

Lighting time delay: 		0 s – 60 min

Lighting standby time:		0 s – 60 min / not active / permanently on

Standby dimming value:	1 – 25%

Presence switch-on delay: 	0 s – 120 min / not active

Presence time delay: 		0 s – 120 min

Temperature sensor:		-15 – +60 °C

Protection rating: 		IP20

Operating temperature: 		-5 °C to +45 °C

Dimensions: 			Ø 860 mm, installation depth 37 mm

Installation: 		ceiling installation in flush-mounted box size 1 or ceiling installation socket 73A

Installation: 			Ceiling installation possible with surface frame thePixa WH

Optional accessories:

### Surface frame thePixa WH

Order No. white: 		9070816

### Ceiling installation box 68A

Drill diameter 68 mm

Order No.: 			9070992