# Tender text

# Presence detector theRonda P360 DALI-2 HCL UP WH

Order No. white: 		2080095

Features:

- Passive infrared presence detector DALI-2 for automatic presence and brightness-dependent control of lighting and other systems

- Detection range round 360 °, walking up to 491 m2 (Ø 25 m)

- This device evaluates the information from the DALI push button interfaces and controls the actuators such as DALI ballasts or DALI relays in accordance with the DALI-2 standard

- Integrated DALI supply

- Colour temperature control based on the time of day HCL (Human Centric Lighting)

- Operation with RGBW lamps

- Time-controlled actions thanks to the integrated time switch

- Flexible assignment of up to 4 lighting groups, plus up to 4 switching groups and 2 presence groups via app

- Constant light control or dimmable lighting in switching mode with and without the influence of daylight, orientation light

- Switching operation and constant light control without the influence of presence

- 3 light measurements

- Simple adjustment of the brightness measurement by entering the measured value Lux

- Easy integration of up to 4 DALI push button interfaces (16 push buttons) via app

- Simple, intuitive commissioning and operation thanks to app, bidirectional communication via BLE and thus easy reading of all parameters

- Connection protection to protect against third-party tampering

- Scenes can be created with any DALI ballasts and called up using push buttons or remote control

- Operation switchable as fully automatic or semi-automatic device

- Dimming speed manual dimming can be set in 2 levels

- Selection of the dimming curve (normal or linear dimming curve according to IEC 62386-218)

- Self-learning time delay

- Reduction of time delay when present briefly (short-term presence)

- Teach-in function

- Detection sensitivity adjustable

- Extremely simple setting of the energy-saving behaviour (eco / eco plus)

- Selectable constant light control speed

- Manual override via remote control or push button

- Staircase light function

- Selectable behaviour upon push button operation (school, office)

- Test mode to check function and detection area

- Test mode light

- Status display via RGB LED

- Nice design with changeable cover frames in three colours

- Simple expansion of the detection range through automatic integration of the DALI-2 presence sensors

- App "DALI-2 RSplug" (for iOS / Android / Windows)

- Ceiling installation in flush-mounted box size 1 or with ceiling installation box 68A with spring springs (optional)

- Surface mounting possible with surface frame 110A (optional)

- User remote control "theSenda B" (optional)

- Detection range restriction with cover clips (optional)

- This device complies with the EMC directive 2014/30 / EU, NSR 2014/35 / EU and EN 62386-101/102 and supported 208/209/218/301/303

Technical data:

Operating voltage: 			230 V AC, +10 %/–15 %, 50 Hz

Power consumption: 			< 0,7 W (without DALI participants)

< 1.6 W (with DALI output 150 mA)

DALI output: 				guaranteed 150 mA, max. 250 mA (according to EN 62386-101)

Detection range sitting: 			Ø 6 m (installation height 3 m)

Detection range walking: 		Ø 24 m tangential, Ø 8 m radial (installation height 3 m)

Installation height: 			2 – 15 m

Adjustable brightness: 			10 – 6’000 lux / measurement off

Switch-off delay time light: 		10 s - 120 min

Standby time: 				0 s - 180 min / permanently on

Standby dimming value: 		1 - 75% stepless

Switch-on delay time presence: 		0 s - 10 min

Switch-off delay time presence: 		10 s - 120 min

Time accuracy of time switch: 		≤ ± 0.5 s / day at + 25 ° C

Power reserve of time switch: 			7 years

Protection rating:			IP 54 (when installed)

Operating temperature:		 	-15° C … +45 °C

Dimensions: 				Ø 110 mm, installation depth 40 mm

Connection type: 			screw terminals / max. 2 x 2.5 mm2

Optional accessories:

Extension of the detection range theRonda P360 DALI-2 S UP WH, Ø 24 m

Order No.: white: 		2080090

Extension of the detection range theRonda S360 DALI-2 S UP WH, Ø 8 m

Order No.: white: 		2080590

Extension of the detection range thePassa P360 DALI-2 S UP WH, 30 m x 4,5 m

Order No.: white: 		2010390

Extension of the detection range PlanoSpot 360 DALI-2 S DE WH, 7 m x 7 m

Order No.: white: 		2030190

DALI-2 push button interface TA 4 S DALI-2

Compact flush-mounted DALI-2 control device with 4 inputs for connecting potential-free push buttons in accordance with IEC 62386 part 301.

Order No.:  			4960094

DALI-2 switch actuator SU DALI-2

Compact flush-mounted DALI-2 relay module for direct control of loads via the DALI bus according to IEC 62386 part 208 (device type 7). Potential-free µ-contact, 13 A / 250 V AC.

Order No.:   			4940091

### User remote control theSenda B

User remote control with integrated lux meter.

Order No.:    			9070985

### Surface frame 110A

Order no. white: 		9070912 (surface frame 110A WH)

Order No. grey: 		9070913 (surface frame 110A GR)

Order No. black: 		9070600 (surface frame 110A BK)

### Cover frame 110

Order No. grey: 		9070591 (cover frame 110 grey)

Order No. black: 		9070851 (cover frame 110 black)

### Ceiling installation box 68A

Drill diameter 68 mm

Order No.: 			9070992

### Cover clip for detection range restriction

5 pieces

Order No.: 			9070921

QuickSafe ball protection

Order No.:  			9070531