# Tender text

# Motion detector theMova S360-100 FLAT DE WH

Order no. white: 		1030540

Features:

- Passive infrared motion detector for ceiling installation

- Automatic motion and brightness-dependent control for lighting

- Circular detection area 360°, moving up to 64 m2 (Ø 9 m)

- Daylight sensor mode for brightness-dependent control of the lighting, switchable via app

- Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs

- Operation as fully automatic device

- Brightness setpoint adjustable, teach-in function

- Reduction of time delay when present briefly (short-term presence)

- Pulse function for staircase light timer switch

- Configurable detection sensitivity

- Ready for immediate use due to factory presetting

- Can be configured remotely with remote control

- Test mode for checking function and detection area

Technical data:

Operating voltage: 		230 V AC

Frequency: 			50 Hz

Power consumption: 		approx. 0.5 W

Moving detection area: 	Ø 8 m tangential, Ø 4 m radial (IH 3 m)

Installation height (IH): 		2 – 4 m

Lighting channel A: 		relay, 1 NO contact 230 V / 10 A, 2300 W or 1150 VA (cos ϕ = 0.5)

Max. LED switching capacity:	250 W

Max. inrush current:		400 A / 200 µs

Brightness switching value: 	30 – 3000 lux

Lighting time delay: 		10 s – 60 min

Protection rating: 		IP 54 (when installed)

Operating temperature: 		-15 °C to +50 °C

Dimensions: 			Ø 85 mm, installation depth 74 mm

Installation: 			in hollow ceilings with springs, ceiling cut-out Ø 62 – 70 mm

Optional accessories:

### theSenda B universal remote control

User remote control with integrated luxmeter.

Remote control for installers: the free theSenda Plug app is easy to use for commissioning or adjusting the parameters. Parameter sets can be saved and named in a customer-specific way and exported for archiving, for instance via email.

Order no.: 			9070985

### theSenda P service remote control

Order no.: 			9070910

### theSenda S user remote control

Order no.: 			9070911

### Cover 85 GR cover clip

Order no.: 			9070594 (grey)