Draft:

EIB/KNX Fan coil actuator, basic device, for fan coil, 1 channel (FCA 1)

Series device, width 72 mm, controls fan coils with up to 3 fan stages (8 A) and the heating/ cooling valve (triacs). 2-pipe and 4-pipe systems are supported. And at the same time it actuates 2 point and 3 point valves. An additional relay (16 A) enables the actuation of an electrical heater bank or alternatively an electrical cooler bank.

Includes 2 floating inputs for window contact and condensate monitoring. The window contact input can be reconfigured as a temperature sensor input.

Operating status is displayed via 9 LEDs.

With filter change object.

Emergency program in case of bus or telegram failure; LED switching status display and operating keys for start up. One key for fan stages and one for switching between heating and cooling.

Deliver, assemble, connect up and set up

Make: Theben

Type: FCA 1 EIB/KNX

Order No.: 4920200

Unit: ST