# Tender text for presence detectors

# Presence detectors for ceiling installation PlanoCentro 201 -UWH / UBK / USR

Passive infrared presence detector for flush-mount/surface-mount installation; flat design, with metal installation frame for screw attachment in flush-mount/surface-mount socket for concrete ceiling, plaster ceiling or wooden ceiling; square 360° detection area, walking 100 m2 (10 x 10 m), seated 64 m2 (8 x 8 m) at 3.5 m installation height;

Automatic presence and brightness-dependent control for lighting and HVAC; can be switched between fully automatic or semi-automatic operation; mixed light measurement approx. 10 - 2000 Lux;

Operating voltage 230 V AC / 50 Hz;

Channels A, B light: relay closer, 230 V / 10 A, 2300 W, zero cross switching, switch-off delay 10 s – 60 min, staircase light function, connection option for push buttons or switches for manual switching with automatic recognition of push button/switch;

Channel H, presence: relay closer, floating, 60 W / 220 V DC or 62 VA / 250 V AC, switch-off delay 10 s – 120 min, switch-on delay 0 s – 10 min / room monitoring;

6 defined parameter basic settings direct on the device, configurable sensitivity; remotely configurable and reading of the set parameters;

Installation cut-out section 100 x 100 mm, cover white (UWH), black (UBK), silver (USR) 112 x 112 x 5 mm, can be changed according to design, colour and material; protection rating IP 40 in fitted state

Manufacturer: thebenHTS

Type: PlanoCentro 201 U..

Order No.:	203 0 602 (PlanoCentro 201-UWH, white, similar to RAL 9010)

203 0 603 (PlanoCentro 201-UBK, black, similar to RAL 9005)

203 0 604 (PlanoCentro 201-USR, silver, similar to RAL 9006)

Unit: ST

### Accessories

### SendoPro 868-A management remote control

Optional for the installer for start-up or adjustment to usage conditions.

Text-based operator guidance in the display. Transmission of individual settings or complete configuration sets to the detector possible. Option of calling up pre-defined parameter sets. Suitable for all remote controlled thebenHTS presence detectors.

Order No.: 9070675

### SendoClic user remote control

optional

Order No.: 9070690

### Flush-mounted socket, 115 x 115 x 100 mm

Agro/Kaiser flush-mounted junction box 9908.01

Order No.: 9070689