# Presence detectors with pre-assembled Wieland GST connectors

# 1 channel presence detector theRonda S360-100 WH GST

Passive-infrared motion detector for ceiling installation; automatic presence and brightness-dependent control for lighting; round 360° detection area, walking up to 64 m2 (Ø 9 m), installation height up to 4 m;

Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs;

Operating voltage 230V AC / 50Hz; Protection rating IP 20, in fitted state IP 54; operating temperature -15ºC to +50ºC;

Channel A light: relay, 1 NO contact 230V / 10A, 2300W or 1150VA (cos ϕ = 0.5), switch-on current max. 400A / 200µs; fully automatic device; configurable brightness switching value approx. 30 – 3000 Lux, teach-in function; time delay 10 sec. – 60 min; pulse function for staircase light timer switch;

Configurable sensitivity; ready for operation immediately thanks to factory presetting; can be configured remotely with remote control; test mode to check function and detection area;

Installation in hollow ceilings with springs, ceiling cut-out Ø 62 – 70 mm, installation depth 74 mm;

Make: Theben

Type: theRonda S360-100 WH GST (White)

Order no.: 2080570

Unit: ST

### Accessories

### Management remote control "SendoPro 868-A"

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order no.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911