# Tender text for presence detectors

# Presence detector thePrema S360 DALI UP WH / GR

Passive-infrared presence detector for ceiling installation; automatic presence and brightness-dependent lighting control with constant lighting control or switching mode; square 360° detection area, walking 49 m2 (7 x 7 m), seated 25 m2 (5 x 5 m) at 3 m installation height;

Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs;

Operating voltage 230 V AC / 50 Hz, power consumption approx. 0.5 W; protection class IP 20, IP 40 when installed; DALI interface in accordance with EN 62386:2009 for max. 25 DALI devices; easy start-up without programming of group addresses (DALI Broadcast);

Constant lighting control with standby function, dimmable lighting in switching operation with standby function; standby brightness of 1 – 25 % adjustable as orientation light; operation switchable as fully automatic or semi automatic device; adjustable brightness setpoint value approx. 5 – 3000 lux, teach-in function via remote control or button; self-learning time delay 10 s – 60 min; reduction of time delay when present briefly (short-term presence); connection option for buttons for manual dimming and switching; selectable behaviour upon button operation; scene functionality; setting of the room correction factor for adjustment of the brightness measurement; adjustable detection sensitivity;

Ready for operation immediately thanks to factory presets; can be configured remotely with remote control; extremely simple configuration of energy-saving behaviour with the new "eco plus" function; test mode to check function and detection area; extension of detection area by master/slave or master/master switching;

Installation depth 40 mm, ceiling installation in flush-mounted box size 1 or ceiling installation socket 73A, ceiling installation possible with back box 110A;

Manufacturer: thebenHTS

Type: thePrema S360 DALI UP..

Order no.: 2070525 (thePrema S360 DALI UP WH, white)

2070526 (thePrema S360 DALI UP GR, grey)

Unit: ST

### Accessories

Extension of detection area via slave device:

Optional

Type: thePrema S360 Slave E UP..

Order no.: 2070630 (thePrema S360 Slave E UP WH, white)

2070631 (thePrema S360 Slave E UP GR, grey)

### Management remote control "SendoPro 868-A"

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order no.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911

### Back box 110A WH

Optional

Order no.: 9070912

### Back box 110A GR

Optional

Order no.: 9070913

### Ceiling installation socket 73A

Optional

Drill diameter 73 mm

Order no.: 9070917