# Tender text for DALI presence detectors

# Presence detector theRonda P360-330 DALI UP WH / GR

Passive-infrared presence detector for ceiling installation; automatic presence and brightness-dependent lighting control with constant lighting control or switching mode; round 360° detection area, walking 452 m2 (Ø 24 m), seated 38 m2 (Ø 7 m) at 3 m installation height; installation height up to 10 m, range restriction with covering clips (optional);

Mixed light measurement with 3 directed light measurements for fluorescent lamps (FL/PL/ESL), suitable for halogen/incandescent lamps and LEDs;

Operating voltage 110 - 230 V AC / 50 - 60 Hz, energy consumption approx. 0.3 W; protection rating IP 54 (in fitted state); DALI interface in accordance with EN 62386 for max. 50 DALI devices;

Up to 3 lighting channels can be addressed; simple, intuitive configuration of the DALI groups via button or remote control; constant lighting control or dimmable lighting in switching operation with or without effect of daylight; standby functionality; fully variable standby dimming value of 1 - 25% as orientation light; operation switchable as fully automatic or semi-automatic device; adjustable brightness setpoint value approx. 10 - 3000 lux, teach-in function via remote control or button; self-learning time delay 10 s - 60 min; reduction of time delay when present briefly (short-term presence); connection option for up to 3 conventional buttons for manual dimming and switching; flexible assignment of the buttons to the required lighting channel via remote control; selectable behaviour upon button operation (school, office); scene functionality; easy adjustment of the brightness measurement with input of the measured lux value (room correction factor); adjustable detection sensitivity; can be configured remotely with remote control; "eco plus" function makes it extremely easy to set energy-saving behaviour; test mode to check function and detection area; extension of detection area by master-slave or master-master switching;

Installation depth 40 mm, ceiling installation in flush-mounted box size 1 or ceiling installation socket 73A, ceiling installation possible with back box 110A;

Manufacturer: thebenHTS

Type: theRonda P360-330 DALI UP..

Order no.: 2080045 (theRonda P360-330 DALI UP WH, White)

2080046 (theRonda P360-330 DALI UP GR, Grey)

Unit: ST

### Accessories

Extension of detection area via slave device:

Optional

Type: theRonda P360 Slave UP..

Order no.: 2080030 (theRonda P360 Slave UP WH, White)

2080031 (theRonda P360 Slave UP GR, Grey)

### Management remote control "SendoPro 868-A"

Optional (required for commissioning!)

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote-controlled thebenHTS presence detectors.

Order no.: 9070675

### User remote control "theSenda S"

Optional

Order no.: 9070911

### Back box 110A WH

Optional

Order no.: 9070912

### Back box 110A GR

Optional

Order no.: 9070913

### Ceiling installation socket 73A

Optional

Drill diameter 73 mm

Order no.: 9070917

### Cover clip for area restriction

Optional

Order no.: 9070921